## Slide 1: skysparkEDA_0103
Yujie Xu

## Slide 2
Tasks completed
  Finished downloading 2018 sparks rules data for all buildings
  Summary statistics of the above

## Slide 3
Presence of rule data

## Slide 4
According to the skyspark interface, there are 153 buildings with GSALink. Among them 89 buildings have spark rules triggered in 2018.
status | building count
downloaded | 89
no data | 64

## Slide 5: 2018 Rule data by building

## Slide 6: 2018 Rule data top 10 by number of buildings affected
rule | # buildings
Missing Data | 89
Sensor Out Of Range | 80
AHU Cooling Valve Unstable | 72
AHU Discharge Temperature Setpoint Unreachable | 71
Sensor Failure | 68
Pump Cycling | 65
AHU Cooling Failure | 63
AHU Damper Unstable | 63
AHU Excessive Discharge Fan Speed | 63
AHU Discharge Pressure Setpoint Unreachable | 62

## Slide 7: 2018 Rule data top 10 by total duration (hour)
rule | total duration
Missing Data | 14,459,366.2
Sensor Out Of Range | 6,131,217.5
Unoccupied Cooling Setpoint Out of Range | 1,732,170.1
Sensor Failure | 1,725,016.0
Terminal Unit Airflow Setpoint Unreachable | 511,831.7
Bad Energy Data | 284,025.3
AHU Discharge Pressure Setpoint Unreachable | 236,682.7
AHU Discharge Temperature Setpoint Unreachable | 175,349.6
Occupied Zone Temperature Out of Range | 159,031.1
AHU Excessive Discharge Fan Speed | 144,380.1

## Slide 8: 2018 Rule data top 10 by highest cost
rule | total cost
Excessive Water Usage During Unoccupancy | 15,885,511
Missing Data | 14,459,385
Short Demand Peak | 6,201,089
Sensor Out Of Range | 6,131,217
AHU Cooling Valve Leaking | 3,024,359
AHU Heating Valve Leaking | 2,525,791
Unoccupied Cooling Setpoint Out of Range | 2,141,762
Sensor Failure | 1,725,016
AHU Discharge Pressure Setpoint Unreachable | 1,656,767
AHU Discharge Temperature Setpoint Unreachable | 1,584,112
2018 Rule data top 10 by highest cost

## Slide 9: Rankings using the same three criteria above but excluding sensor or data related rules: “Missing Data”, “Sensor Out Of Range”, “Sensor Failure”, and “Bad Energy Data”

## Slide 10
rule | # buildings
AHU Cooling Valve Unstable | 72
AHU Discharge Temperature Setpoint Unreachable | 71
Pump Cycling | 65
AHU Cooling Failure | 63
AHU Damper Unstable | 63
AHU Excessive Discharge Fan Speed | 63
AHU Discharge Pressure Setpoint Unreachable | 62
AHU Heating Valve Unstable | 62
Maximum Demand During Unoccupancy | 60
AHU Cooling Valve Leaking | 58
2018 Rule data top 10 by # buildings affected (excluding data error)

## Slide 11
rule | total duration
Unoccupied Cooling Setpoint Out of Range | 1,732,170.11
Terminal Unit Airflow Setpoint Unreachable | 511,831.67
AHU Discharge Pressure Setpoint Unreachable | 236,682.69
AHU Discharge Temperature Setpoint Unreachable | 175,349.60
Occupied Zone Temperature Out of Range | 159,031.07
AHU Excessive Discharge Fan Speed | 144,380.12
AHU Discharge Fan Failure | 138,340.15
AHU Cooling Valve Leaking | 111,486.62
AHU Cooling Failure | 92,739.32
Occupied Cooling Setpoint Out of Range | 92,530.33
2018 Rule data top 10 by total duration (excluding data error)

## Slide 12
rule | total cost
Excessive Water Usage During Unoccupancy | 15,885,511
Short Demand Peak | 6,201,089
AHU Cooling Valve Leaking | 3,024,359
AHU Heating Valve Leaking | 2,525,791
Unoccupied Cooling Setpoint Out of Range | 2,141,762
AHU Discharge Pressure Setpoint Unreachable | 1,656,767
AHU Discharge Temperature Setpoint Unreachable | 1,584,112
Occupied Cooling Setpoint Out of Range | 1,529,597
AHU Cooling & Heating Simultaneously | 1,529,441
AHU Outside Damper Stuck Open | 1,477,591
2018 Rule data top 10 by highest cost (excluding data error)

## Slide 13: 20 Rules show up in at least one of the criteria, and 3 Rules show up in all three criteria

## Slide 14
20 Rules show up in at least one of the criteria
## [1] "AHU Cooling & Heating Simultaneously" ## [2] "AHU Cooling Failure" ## [3] "AHU Cooling Valve Leaking" ## [4] "AHU Cooling Valve Unstable" ## [5] "AHU Damper Unstable" ## [6] "AHU Discharge Fan Failure" ## [7] "AHU Discharge Pressure Setpoint Unreachable" ## [8] "AHU Discharge Temperature Setpoint Unreachable" ## [9] "AHU Excessive Discharge Fan Speed" ## [10] "AHU Heating Valve Leaking" ## [11] "AHU Heating Valve Unstable" ## [12] "AHU Outside Damper Stuck Open" ## [13] "Excessive Water Usage During Unoccupancy" ## [14] "Maximum Demand During Unoccupancy" ## [15] "Occupied Cooling Setpoint Out of Range" ## [16] "Occupied Zone Temperature Out of Range" ## [17] "Pump Cycling" ## [18] "Short Demand Peak" ## [19] "Terminal Unit Airflow Setpoint Unreachable" ## [20] "Unoccupied Cooling Setpoint Out of Range"

## Slide 15
3 Rules show up in all three criteria
## [1] "AHU Cooling Valve Leaking" ## [2] "AHU Discharge Pressure Setpoint Unreachable" ## [3] "AHU Discharge Temperature Setpoint Unreachable"