## Slide 1: skysparkEDA_0103
Yujie Xu

## Slide 2: Tasks completed
  Finished downloading 2018 sparks rules data for all buildings
  Summary statistics of the above

## Slide 3: Presence of rule data
According to the skyspark interface, there are 153 buildings with GSALink. Among them 89 buildings have spark rules triggered in 2018.
status | building count
downloaded | 89
no data | 64

## Slide 4: 2018 Rule data by building

## Slide 5
building | # rules | count | total cost | total duration
PA0277BG | 7 | 36,638 | 1,162,010.9 | 877,379.8
PA0278BG | 4 | 40,948 | 1,142,800.9 | 980,182.0
MD0278ZZ | 31 | 63,638 | 1,092,953.8 | 705,839.6
TX0250AU | 21 | 24,196 | 892,153.9 | 469,827.7
AL0039AB | 36 | 29,363 | 846,491.4 | 668,626.4
DC1473SE | 30 | 4,556 | 814,465.2 | 42,941.8
NM0061ZZ | 24 | 43,232 | 804,162.5 | 896,988.4
NY0128ZZ | 34 | 26,588 | 769,672.8 | 322,759.5
GA0010AE | 27 | 16,003 | 685,932.4 | 239,292.1
MA0131ZZ | 27 | 14,987 | 671,693.2 | 267,139.9
IN0048ZZ | 39 | 17,094 | 665,795.8 | 174,946.0
IN0133ZZ | 33 | 6,942 | 660,276.1 | 133,152.1
IL0236FC | 33 | 13,496 | 652,092.8 | 131,867.0

## Slide 6
building | # rules | count | total cost | total duration
IL0236FC | 33 | 13,496 | 652,092.8 | 131,867.0
TN0088ZZ | 25 | 6,755 | 649,552.0 | 79,218.2
AL0076AB | 21 | 26,926 | 636,667.9 | 587,928.8
IL0032ZZ | 36 | 10,012 | 609,306.8 | 162,770.5
DC0084ZZ | 21 | 6,082 | 579,588.9 | 73,711.6
MI0029ZZ | 30 | 5,457 | 541,877.2 | 68,872.3
TX0284DA | 33 | 9,815 | 534,538.6 | 168,787.2
UT0032ZZ | 25 | 20,265 | 531,087.7 | 461,917.1
IL0205ZZ | 40 | 6,974 | 509,432.6 | 87,707.0
OH0189CN | 27 | 8,431 | 481,721.0 | 165,320.1
TX0302ZZ | 20 | 7,579 | 471,778.9 | 119,378.2
CO0009ZZ | 35 | 11,697 | 450,450.6 | 224,106.1
DC0083ZZ | 20 | 8,003 | 446,066.9 | 127,784.8

## Slide 7
building | # rules | count | total cost | total duration
DC0083ZZ | 20 | 8,003 | 446,066.9 | 127,784.8
GA1007ZZ | 20 | 9,698 | 436,579.5 | 147,115.1
OH0033ZZ | 18 | 3,530 | 383,653.8 | 41,214.0
MS0083ZZ | 32 | 11,980 | 378,688.2 | 169,845.4
NM0050ZZ | 23 | 4,589 | 369,191.2 | 32,287.6
UT0017ZZ | 32 | 12,033 | 337,994.1 | 269,789.5
NY0304ZZ | 29 | 13,647 | 300,967.9 | 204,688.1
CA0306ZZ | 39 | 5,602 | 292,698.6 | 59,980.9
CO0061ZZ | 31 | 8,074 | 288,509.0 | 116,585.1
FL0067ZZ | 22 | 9,353 | 285,018.9 | 170,112.3
CO0054ZZ | 29 | 5,639 | 257,391.9 | 72,506.3
NY0300ZZ | 30 | 5,362 | 253,979.6 | 90,709.1
MO0050ZZ | 33 | 7,758 | 248,098.1 | 85,039.0

## Slide 8
building | # rules | count | total cost | total duration
MO0050ZZ | 33 | 7,758 | 248,098.1 | 85,039.0
DC0021ZZ | 21 | 2,479 | 231,959.8 | 38,468.1
MO0095ZZ | 34 | 6,448 | 227,398.5 | 93,750.7
WY0029ZZ | 33 | 8,082 | 225,270.0 | 103,285.0
CA0154ZZ | 25 | 3,361 | 206,899.4 | 40,156.9
OH0028CN | 29 | 7,333 | 206,480.5 | 79,446.6
TX0224ZZ | 32 | 5,801 | 202,654.9 | 87,124.1
OR0043ZZ | 27 | 3,543 | 194,168.1 | 45,370.8
TX0058DA | 15 | 6,111 | 193,044.9 | 108,487.1
MN0087ZZ | 18 | 11,552 | 189,617.7 | 150,792.0
CA0305ZZ | 24 | 3,492 | 169,764.0 | 50,651.7
TX0057ZZ | 30 | 3,633 | 163,377.8 | 31,653.2
IA0112ZZ | 32 | 2,280 | 150,014.6 | 28,265.1

## Slide 9
building | # rules | count | total cost | total duration
IA0112ZZ | 32 | 2,280 | 150,014.6 | 28,265.1
OH0194ZZ | 26 | 3,599 | 137,961.7 | 60,567.1
CO0516AA | 30 | 5,328 | 135,807.6 | 100,312.0
AR0030RK | 31 | 3,742 | 129,976.4 | 41,815.6
WA0961KC | 25 | 4,074 | 108,530.2 | 72,985.8
OR0033PE | 35 | 4,025 | 105,195.6 | 63,677.3
KS0094ZZ | 22 | 5,112 | 86,611.2 | 52,318.9
ND0006ZZ | 11 | 2,060 | 85,727.9 | 40,594.3
IA0121ZZ | 24 | 2,535 | 83,906.0 | 30,628.9
OR0052ZZ | 19 | 3,260 | 83,827.9 | 36,905.0
NE0531ZZ | 30 | 3,331 | 73,658.1 | 47,992.6
OK0101ZZ | 25 | 2,098 | 64,483.8 | 28,977.7
TX0501HS | 23 | 2,739 | 57,949.3 | 33,558.8

## Slide 10
building | # rules | count | total cost | total duration
TX0501HS | 23 | 2,739 | 57,949.3 | 33,558.8
CA0096DD | 25 | 2,550 | 54,169.7 | 37,692.1
NE0051ZZ | 25 | 2,722 | 52,589.1 | 35,876.1
OK0046CT | 27 | 2,766 | 48,636.4 | 22,468.3
OH0046ZZ | 31 | 1,783 | 47,151.1 | 14,784.0
NE0036ZZ | 22 | 2,814 | 44,051.1 | 34,615.4
CA0091AA | 22 | 1,338 | 36,850.7 | 27,291.7
AK0031AA | 10 | 237 | 34,406.6 | 3,219.0
NM0030ZZ | 26 | 845 | 31,380.7 | 8,007.2
MA0153ZZ | 13 | 877 | 23,397.5 | 17,852.3
IL0235FC | 10 | 499 | 22,367.5 | 6,896.5
IL0303ZZ | 16 | 735 | 21,563.7 | 14,034.5
DC0033ZZ | 1 | 586 | 14,068.0 | 14,068.0

## Slide 11
building | # rules | count | total cost | total duration
DC0033ZZ | 1 | 586 | 14,068.0 | 14,068.0
TX0227AU | 1 | 451 | 8,795.9 | 8,795.9
DC0034ZZ | 2 | 268 | 6,434.0 | 6,434.0
DC0010ZZ | 1 | 139 | 3,331.2 | 3,331.2
MD0767AG | 1 | 134 | 3,217.0 | 3,217.0
CA0092AA | 1 | 85 | 1,611.4 | 1,611.4

## Slide 12: top ranking rules based on three criteria

## Slide 13: 2018 Rule data top 10 by number of buildings affected
rule | # buildings
Missing Data | 89
Sensor Out Of Range | 80
AHU Cooling Valve Unstable | 72
AHU Discharge Temperature Setpoint Unreachable | 71
Sensor Failure | 68
Pump Cycling | 65
AHU Cooling Failure | 63
AHU Damper Unstable | 63
AHU Excessive Discharge Fan Speed | 63
AHU Discharge Pressure Setpoint Unreachable | 62

## Slide 14: 2018 Rule data top 10 by total duration (hour)
rule | total duration
Missing Data | 14,459,366.2
Sensor Out Of Range | 6,131,217.5
Unoccupied Cooling Setpoint Out of Range | 1,732,170.1
Sensor Failure | 1,725,016.0
Terminal Unit Airflow Setpoint Unreachable | 511,831.7
Bad Energy Data | 284,025.3
AHU Discharge Pressure Setpoint Unreachable | 236,682.7
AHU Discharge Temperature Setpoint Unreachable | 175,349.6
Occupied Zone Temperature Out of Range | 159,031.1
AHU Excessive Discharge Fan Speed | 144,380.1

## Slide 15: Most affected buildings
building | name | rule | duration_hour
NY0282ZZ | JACOB K. JAVITS FB/CIT | Missing Data | 4,705,093.9
ND0046ZZ | FB-PO | Missing Data | 2,224,816.2
PA0278BG | JAMES A BYRNE US COURTHOUSE | Missing Data | 957,336.0
NV0304ZZ | LLOYD D. GEORGE COURTHOUSE | Missing Data | 868,889.3
PA0277BG | WM J GREEN JR FB | Missing Data | 866,312.8

## Slide 16
building | name | rule | duration_hour
NV0304ZZ | LLOYD D. GEORGE COURTHOUSE | Sensor Out Of Range | 1,202,399.9
NY0282ZZ | JACOB K. JAVITS FB/CIT | Sensor Out Of Range | 924,745.6
AL0039AB | JOHN A CAMPBELL USCT | Sensor Out Of Range | 572,419.9
AL0076AB | FEDERAL BUILDING | Sensor Out Of Range | 564,770.6
NM0061ZZ | LAS CRUCES COURTHOUSE | Sensor Out Of Range | 534,753.8

## Slide 17
building | name | rule | duration_hour
NV0304ZZ | LLOYD D. GEORGE COURTHOUSE | Unoccupied Cooling Setpoint Out of Range | 997,776.0
NM0061ZZ | LAS CRUCES COURTHOUSE | Unoccupied Cooling Setpoint Out of Range | 241,541.0
OH0192ZZ | A J CELEBREZZE FB | Unoccupied Cooling Setpoint Out of Range | 150,358.5
NY0282ZZ | JACOB K. JAVITS FB/CIT | Unoccupied Cooling Setpoint Out of Range | 93,854.4
CA0167ZZ | EDWARD J. SCHWARTZ FOB & CTHS | Unoccupied Cooling Setpoint Out of Range | 55,392.7

## Slide 18
building | name | rule | duration_hour
MD0278ZZ | NEW CARROLLTON FED | Sensor Failure | 247,189
TX0250AU | HOMER THORNBERRY BLDG | Sensor Failure | 245,602
UT0017ZZ | FRANK E MOSS COURTHOUSE | Sensor Failure | 232,165
AZ0303ZZ | SANDRA D. O’CONNOR COURTHOUSE | Sensor Failure | 191,184
IN0133ZZ | MINTON-CAPEHART F/B | Sensor Failure | 87,240

## Slide 19
building | name | rule | duration_hour
MD0278ZZ | NEW CARROLLTON FED | Terminal Unit Airflow Setpoint Unreachable | 94,043.4
IL0236FC | JOHN C. KLUCZYNSKI FED. BLDG. | Terminal Unit Airflow Setpoint Unreachable | 67,142.0
NC0002AE | VEACH-BALEY FEDERAL COMPLEX | Terminal Unit Airflow Setpoint Unreachable | 37,328.0
TX0250AU | HOMER THORNBERRY BLDG | Terminal Unit Airflow Setpoint Unreachable | 32,732.7
NY0128ZZ | FEDERAL BLDG-201 VA | Terminal Unit Airflow Setpoint Unreachable | 30,229.7

## Slide 20: 2018 Rule data top 10 by highest cost
rule | total cost
Excessive Water Usage During Unoccupancy | 15,885,511
Missing Data | 14,459,385
Short Demand Peak | 6,201,089
Sensor Out Of Range | 6,131,217
AHU Cooling Valve Leaking | 3,024,359
AHU Heating Valve Leaking | 2,525,791
Unoccupied Cooling Setpoint Out of Range | 2,141,762
Sensor Failure | 1,725,016
AHU Discharge Pressure Setpoint Unreachable | 1,656,767
AHU Discharge Temperature Setpoint Unreachable | 1,584,112

## Slide 21: Most affected buildings
building | name | rule | Cost
NY0281ZZ | JAMES M HANLEY FB | Excessive Water Usage During Unoccupancy | 13,026,181.4
NY0282ZZ | JACOB K. JAVITS FB/CIT | Excessive Water Usage During Unoccupancy | 1,135,932.0
OH0192ZZ | A J CELEBREZZE FB | Excessive Water Usage During Unoccupancy | 700,398.6
LA0085ZZ | H BOGGS FED BLDG/COURTHOUSE | Excessive Water Usage During Unoccupancy | 663,526.0
NM0050ZZ | PETE DOMENICI COURTHOUSE | Excessive Water Usage During Unoccupancy | 290,018.4

## Slide 22
building | name | rule | Cost
NY0282ZZ | JACOB K. JAVITS FB/CIT | Missing Data | 4,705,093.9
ND0046ZZ | FB-PO | Missing Data | 2,224,816.2
PA0278BG | JAMES A BYRNE US COURTHOUSE | Missing Data | 957,336.0
NV0304ZZ | LLOYD D. GEORGE COURTHOUSE | Missing Data | 868,889.3
PA0277BG | WM J GREEN JR FB | Missing Data | 866,312.8

## Slide 23
building | name | rule | Cost
TX0211ZZ | B CASEY COURTHOUSE | Short Demand Peak | 6,192,271.3
LA0085ZZ | H BOGGS FED BLDG/COURTHOUSE | Short Demand Peak | 1,902.2
IL0205ZZ | EVERETT M. DIRKSEN | Short Demand Peak | 876.1
GA0010AE | IRS ANNEX | Short Demand Peak | 756.6
NY0128ZZ | FEDERAL BLDG-201 VA | Short Demand Peak | 696.2

## Slide 24
building | name | rule | Cost
NV0304ZZ | LLOYD D. GEORGE COURTHOUSE | Sensor Out Of Range | 1,202,399.9
NY0282ZZ | JACOB K. JAVITS FB/CIT | Sensor Out Of Range | 924,745.6
AL0039AB | JOHN A CAMPBELL USCT | Sensor Out Of Range | 572,419.9
AL0076AB | FEDERAL BUILDING | Sensor Out Of Range | 564,770.6
NM0061ZZ | LAS CRUCES COURTHOUSE | Sensor Out Of Range | 534,753.8

## Slide 25
building | name | rule | Cost
DC1473SE | Douglas A. Munro | AHU Cooling Valve Leaking | 469,362.4
OH0192ZZ | A J CELEBREZZE FB | AHU Cooling Valve Leaking | 329,198.8
NY0282ZZ | JACOB K. JAVITS FB/CIT | AHU Cooling Valve Leaking | 306,838.5
TX0250AU | HOMER THORNBERRY BLDG | AHU Cooling Valve Leaking | 263,080.3
TN0088ZZ | CLIFFORD DAVIS-ODELL HORTON | AHU Cooling Valve Leaking | 220,700.1

## Slide 26: Rankings excluding sensor or data related rules: “Missing Data”, “Sensor Out Of Range”, “Sensor Failure”, and “Bad Energy Data”

## Slide 27: 2018 Rule data top 10 by number of buildings affected
rule | # buildings
AHU Cooling Valve Unstable | 72
AHU Discharge Temperature Setpoint Unreachable | 71
Pump Cycling | 65
AHU Cooling Failure | 63
AHU Damper Unstable | 63
AHU Excessive Discharge Fan Speed | 63
AHU Discharge Pressure Setpoint Unreachable | 62
AHU Heating Valve Unstable | 62
Maximum Demand During Unoccupancy | 60
AHU Cooling Valve Leaking | 58

## Slide 28: 2018 Rule data top 10 by total duration (excluding data error)
rule | total duration
Unoccupied Cooling Setpoint Out of Range | 1,732,170.11
Terminal Unit Airflow Setpoint Unreachable | 511,831.67
AHU Discharge Pressure Setpoint Unreachable | 236,682.69
AHU Discharge Temperature Setpoint Unreachable | 175,349.60
Occupied Zone Temperature Out of Range | 159,031.07
AHU Excessive Discharge Fan Speed | 144,380.12
AHU Discharge Fan Failure | 138,340.15
AHU Cooling Valve Leaking | 111,486.62
AHU Cooling Failure | 92,739.32
Occupied Cooling Setpoint Out of Range | 92,530.33

## Slide 29: 2018 Rule data top 10 by highest cost (excluding data error)
rule | total cost
Excessive Water Usage During Unoccupancy | 15,885,511
Short Demand Peak | 6,201,089
AHU Cooling Valve Leaking | 3,024,359
AHU Heating Valve Leaking | 2,525,791
Unoccupied Cooling Setpoint Out of Range | 2,141,762
AHU Discharge Pressure Setpoint Unreachable | 1,656,767
AHU Discharge Temperature Setpoint Unreachable | 1,584,112
Occupied Cooling Setpoint Out of Range | 1,529,597
AHU Cooling & Heating Simultaneously | 1,529,441
AHU Outside Damper Stuck Open | 1,477,591

## Slide 30: 20 Rules show up in at least one of the criteria, and 3 Rules show up in all three criteria

## Slide 31: 20 Rules show up in at least one of the criteria
## [1] "AHU Cooling & Heating Simultaneously" ## [2] "AHU Cooling Failure" ## [3] "AHU Cooling Valve Leaking" ## [4] "AHU Cooling Valve Unstable" ## [5] "AHU Damper Unstable" ## [6] "AHU Discharge Fan Failure" ## [7] "AHU Discharge Pressure Setpoint Unreachable" ## [8] "AHU Discharge Temperature Setpoint Unreachable" ## [9] "AHU Excessive Discharge Fan Speed" ## [10] "AHU Heating Valve Leaking" ## [11] "AHU Heating Valve Unstable" ## [12] "AHU Outside Damper Stuck Open" ## [13] "Excessive Water Usage During Unoccupancy" ## [14] "Maximum Demand During Unoccupancy" ## [15] "Occupied Cooling Setpoint Out of Range" ## [16] "Occupied Zone Temperature Out of Range" ## [17] "Pump Cycling" ## [18] "Short Demand Peak" ## [19] "Terminal Unit Airflow Setpoint Unreachable" ## [20] "Unoccupied Cooling Setpoint Out of Range"

## Slide 32: 3 Rules show up in all three criteria
## [1] "AHU Cooling Valve Leaking" ## [2] "AHU Discharge Pressure Setpoint Unreachable" ## [3] "AHU Discharge Temperature Setpoint Unreachable"