Jan 25 meeting prepare

Yujie Xu

1/25/2019

# Top 10 rules by

## mCost

|  |  |
| --- | --- |
| rule | mCost |
| Chilled Water Pressure Setpoint Unreachable | 115,040 |
| AHU Discharge Pressure Setpoint Unreachable | 37,552 |
| AHU Discharge Temperature Setpoint Unreachable | 35,544 |
| AHU Discharge Fan Failure | 30,826 |
| AHU Excessive Discharge Fan Speed | 27,720 |
| Chiller Cycling | 23,849 |
| Chilled Water System Failure | 22,882 |
| Chiller Running During Unoccupied Periods | 22,712 |
| Pump Cycling | 20,195 |
| Heat Exchanger Temp Setpoint Unreachable | 19,668 |

# Buildings with top mCost under top-mCost-rules

|  |  |  |
| --- | --- | --- |
| rule | building | mCost |
| Chilled Water Pressure Setpoint Unreachable | NV0304ZZ | 34,753 |
| Chilled Water Pressure Setpoint Unreachable | TX0302ZZ | 28,182 |
| Chilled Water Pressure Setpoint Unreachable | NY0128ZZ | 18,422 |
| Chilled Water Pressure Setpoint Unreachable | OH0194ZZ | 6,564 |
| Chilled Water Pressure Setpoint Unreachable | CA0167ZZ | 5,264 |
| Chilled Water Pressure Setpoint Unreachable | IL0236FC | 4,087 |
| Chilled Water Pressure Setpoint Unreachable | CO0054ZZ | 3,851 |
| Chilled Water Pressure Setpoint Unreachable | MA0131ZZ | 3,832 |
| Chilled Water Pressure Setpoint Unreachable | TN0088ZZ | 2,751 |
| Chilled Water Pressure Setpoint Unreachable | UT0032ZZ | 2,265 |
| [1] “” |  |  |
| rule | building | mCost |
| AHU Discharge Pressure Setpoint Unreachable | NC0002AE | 7,526 |
| AHU Discharge Pressure Setpoint Unreachable | LA0085ZZ | 3,142 |
| AHU Discharge Pressure Setpoint Unreachable | OH0192ZZ | 3,126 |
| AHU Discharge Pressure Setpoint Unreachable | CA0167ZZ | 2,392 |
| AHU Discharge Pressure Setpoint Unreachable | IN1703ZZ | 2,201 |
| AHU Discharge Pressure Setpoint Unreachable | DC0021ZZ | 1,909 |
| AHU Discharge Pressure Setpoint Unreachable | NY0128ZZ | 1,749 |
| AHU Discharge Pressure Setpoint Unreachable | FL0067ZZ | 1,578 |
| AHU Discharge Pressure Setpoint Unreachable | NM0050ZZ | 1,356 |
| AHU Discharge Pressure Setpoint Unreachable | GA1007ZZ | 1,205 |
| [1] “” |  |  |
| rule | building | mCost |
| AHU Discharge Temperature Setpoint Unreachable | OH0192ZZ | 6,144 |
| AHU Discharge Temperature Setpoint Unreachable | NC0002AE | 4,780 |
| AHU Discharge Temperature Setpoint Unreachable | GA1007ZZ | 2,896 |
| AHU Discharge Temperature Setpoint Unreachable | GA0010AE | 2,015 |
| AHU Discharge Temperature Setpoint Unreachable | IN1703ZZ | 1,513 |
| AHU Discharge Temperature Setpoint Unreachable | TX0211ZZ | 1,422 |
| AHU Discharge Temperature Setpoint Unreachable | CA0167ZZ | 1,363 |
| AHU Discharge Temperature Setpoint Unreachable | DC0021ZZ | 1,137 |
| AHU Discharge Temperature Setpoint Unreachable | IL0205ZZ | 1,134 |
| AHU Discharge Temperature Setpoint Unreachable | NY0128ZZ | 1,005 |
| [1] “” |  |  |
| rule | building | mCost |
| AHU Discharge Fan Failure | AZ0303ZZ | 14,440 |
| AHU Discharge Fan Failure | NC0002AE | 5,693 |
| AHU Discharge Fan Failure | IN1703ZZ | 1,992 |
| AHU Discharge Fan Failure | CA0167ZZ | 1,424 |
| AHU Discharge Fan Failure | NY0304ZZ | 1,026 |
| AHU Discharge Fan Failure | NY0128ZZ | 750 |
| AHU Discharge Fan Failure | DC0021ZZ | 681 |
| AHU Discharge Fan Failure | IL0236FC | 670 |
| AHU Discharge Fan Failure | GA0010AE | 615 |
| AHU Discharge Fan Failure | CO0009ZZ | 583 |
| [1] “” |  |  |
| rule | building | mCost |
| AHU Excessive Discharge Fan Speed | MA0131ZZ | 4,083 |
| AHU Excessive Discharge Fan Speed | LA0085ZZ | 3,622 |
| AHU Excessive Discharge Fan Speed | NC0002AE | 2,880 |
| AHU Excessive Discharge Fan Speed | OH0189CN | 1,848 |
| AHU Excessive Discharge Fan Speed | DC0021ZZ | 1,364 |
| AHU Excessive Discharge Fan Speed | NY0281ZZ | 1,158 |
| AHU Excessive Discharge Fan Speed | OH0028CN | 998 |
| AHU Excessive Discharge Fan Speed | OH0192ZZ | 933 |
| AHU Excessive Discharge Fan Speed | MO0050ZZ | 856 |
| AHU Excessive Discharge Fan Speed | IL0205ZZ | 815 |
| [1] “” |  |  |
| rule | building | mCost |
| Chiller Cycling | OH0033ZZ | 19,810 |
| Chiller Cycling | NY0128ZZ | 1,038 |
| Chiller Cycling | NC0002AE | 563 |
| Chiller Cycling | TX0224ZZ | 453 |
| Chiller Cycling | IL0032ZZ | 239 |
| Chiller Cycling | OH0192ZZ | 213 |
| Chiller Cycling | TX0211ZZ | 207 |
| Chiller Cycling | AR0030RK | 191 |
| Chiller Cycling | NM0050ZZ | 179 |
| Chiller Cycling | OH0194ZZ | 105 |
| [1] “” |  |  |
| rule | building | mCost |
| Chilled Water System Failure | GA0010AE | 17,936 |
| Chilled Water System Failure | TX0302ZZ | 3,792 |
| Chilled Water System Failure | CA0167ZZ | 367 |
| Chilled Water System Failure | NC0002AE | 286 |
| Chilled Water System Failure | AR0030RK | 277 |
| Chilled Water System Failure | MA0131ZZ | 75 |
| Chilled Water System Failure | LA0085ZZ | 37 |
| Chilled Water System Failure | CO0009ZZ | 33 |
| Chilled Water System Failure | KS0094ZZ | 31 |
| Chilled Water System Failure | MO0050ZZ | 18 |
| [1] “” |  |  |
| rule | building | mCost |
| Chiller Running During Unoccupied Periods | NV0304ZZ | 22,712 |
| [1] “” |  |  |
| rule | building | mCost |
| Pump Cycling | OH0192ZZ | 3,837 |
| Pump Cycling | TN0088ZZ | 3,228 |
| Pump Cycling | NC0002AE | 2,168 |
| Pump Cycling | NY0128ZZ | 1,893 |
| Pump Cycling | CA0306ZZ | 1,478 |
| Pump Cycling | TX0224ZZ | 1,027 |
| Pump Cycling | AZ0303ZZ | 997 |
| Pump Cycling | AR0030RK | 963 |
| Pump Cycling | OR0043ZZ | 920 |
| Pump Cycling | OH0028CN | 474 |
| [1] “” |  |  |
| rule | building | mCost |
| Heat Exchanger Temp Setpoint Unreachable | IN0133ZZ | 9,634 |
| Heat Exchanger Temp Setpoint Unreachable | IL0236FC | 7,948 |
| Heat Exchanger Temp Setpoint Unreachable | OH0192ZZ | 1,089 |
| Heat Exchanger Temp Setpoint Unreachable | IA0121ZZ | 405 |
| Heat Exchanger Temp Setpoint Unreachable | OR0043ZZ | 272 |
| Heat Exchanger Temp Setpoint Unreachable | DC0084ZZ | 222 |
| Heat Exchanger Temp Setpoint Unreachable | IL0205ZZ | 42 |
| Heat Exchanger Temp Setpoint Unreachable | OH0046ZZ | 35 |
| Heat Exchanger Temp Setpoint Unreachable | OR0033PE | 16 |
| Heat Exchanger Temp Setpoint Unreachable | AL0039AB | 5 |
| [1] “” |  |  |